## ABOVE GROUND
ONLY FILL IN THE BLUE CELLS. JUST JUMP BY PRESSING "TAB" KEY
TEMPERATURE DECREASE IN ABOVE GROUND INSTALLED PIPES
INPUT DATA |  |  |  | REMARKS
TEMPERATURE MEDIUM |  | (C) | 60
AMBIENT TEMPERATURE |  | (C) | 5
DENSITY MEDIUM |  | Kg/m 3 | 999
FLOW SPEED MEDIUM |  | m/s | 0.6
MASS OF MEDIUM PER METER PIPE LENGTH |  | kg/m | 0.42962
MASS FLOW MEDIUM |  | Kg/s | 0.25777
SPECIFIC HEAT WATER |  | J/Kg.K | 4200
PIPE MATERIAL MEDIUM PIPE (see abbreviation below) | PVC | W/m.K | 0.16 | HEAT CONDUCTIVE COEFFICIENT PIPE WALL
INSULATION MATERIAL (see abbreviation below) |  | W/m.K |  | HEAT CONDUCTIVE COEFFICIENT INSULATION MATERIAL | 1
CONTAINMENT PIPE MATERIAL (see abbreviation below) | PVC | W/m.K | 0.16 | HEAT CONDUCTIVE COEFFICIENT CONTAINMENT PIPE | 0.16
OUTSIDE DIAMETER PIPE |  | mm | 28.6
SDR |  |  | 11
INSIDE DIAMETER PIPE |  | mm | 23.4
OUTSIDE DIAMETER CONTAINMENT PIPE |  | mm | 48.26 |  | 48.26
SDR OF CONTAINMENT PIPE |  |  | 17.2975
INSIDE DIAMETER CONTAINMENT PIPE |  | mm | 42.68 |  | 42.68
AIR SPEED AROUND PIPE |  | m/s | 3
PIPE LENGTH |  | m | 30
STAGNATION TIME |  | hrs | 10 |  | 36000
HEAT TECHNICAL DATA
|  | W/m.K | KJ/Kg.K
| AIR | 0.023 | 1.006
| HDPE | 0.43 | 1.9
| LDPE | 0.33 | 2.3
| OTHER | 0.566 |  | ANY OTHER PIPE- OR INSULATION MATERIAL; FILL IN VALUE !!!!
| PB | 0.23 | 1.8
| PP | 0.22 | 1.67
| PUR | 0.025 |  | PUR Foam 80/100
| PVC | 0.16 | 1.01
| PVDF | 0.12 | 1.38
| SOIL | 2.326
| STEEL | 67 | 0.45
| WATER | 0.582 | 4.2
| ICE |  | 336
RESULTS
TEMPERATURE DECREASE |  | K/m | 0.13067 | DEGREE per METRE
TEMPERATURE DECREASE OVER WHOLE PIPE LENGTH |  | K | 3.92 | DEGREES
SPECIFIC HEAT LOSS |  | W/m | 141.4659 | WATT per METRE
TOTAL HEAT LOSS OVER WHOLE PIPE LENGTH |  | KW | 4.244 | KILOWATT
HEAT TRANSMISSION NUMBER |  | W/m.K | 2.5721 | WATT per METRE per DEGREE
STAGNATING WATER
TIME TILL FREEZING STARTS |  | hrs
PERCENTAGE FROZEN WATER AFTER STAGNATION TIME |  | %
0.38879 | =R
2.1085 | =alfa
0.0014255 | =B
1682.1991 | =t(s)
12.8605 | =Q(v)
305.74

## BELOW GROUND
ONLY FILL IN THE BLUE CELLS. JUST JUMP BY PRESSING "TAB" KEY
TEMPERATURE DECREASE IN FLOWING MEDIUM IN UNDERGROUND PIPE LINES
INPUT DATA |  |  |  | REMARKS
TEMPERATURE MEDIUM |  | (C) | 15
TEMPERATURE GROUND |  | (C) | 25
DENSITY MEDIUM |  | Kg/m 3 | 999
FLOW SPEED MEDIUM |  | m/s | 2
MASS OF MEDIUM PER METER PIPE LENGTH |  | kg/m | 0.32827
MASS FLOW MEDIUM |  | Kg/s | 0.65655
SPECIFIC HEAT MEDIUM |  | J/Kg.K | 4200
PIPE MATERIAL MEDIUM PIPE (see abbreviation below) | hdpe | W/m.K | 0.43 | HEAT CONDUCTIVE COEFFICIENT PIPE WALL
INSULATION MATERIAL (see abbreviation below) |  | W/m.K |  | HEAT CONDUCTIVE COEFFICIENT INSULATION MATERIAL | 1
CONTAINMENT PIPE MATERIAL (see abbreviation below) |  | W/m.K |  | HEAT CONDUCTIVE COEFFICIENT CONTAINMENT PIPE | 1
HEAT CONDUCTIVE COEFFICIENT GROUND | other | W/m.K | 1.6
OUTSIDE DIAMETER PIPE |  | mm | 25
SDR |  |  | 11
INSIDE DIAMETER PIPE |  | mm | 20.4545
OUTSIDE DIAMETER CONTAINMENT PIPE |  | mm |  |  | 25
SDR OF CONTAINMENT PIPE
INSIDE DIAMETER CONTAINMENT PIPE |  | mm | #DIV/0! |  | 25
DEPTH OF SOIL COVER |  | m | 1
PIPE LENGTH |  | m | 500
STAGNATION TIME |  | hrs |  |  | 0
HEAT TECHNICAL DATA
|  | W/m.K | KJ/Kg.K
| AIR | 0.023 | 1.006
| Concrete | 1.512
| HDPE | 0.43 | 1.9
| LDPE | 0.33 | 2.3
| OTHER | 1.6 |  | ANY OTHER PIPE- OR INSULATION MATERIAL; FILL IN VALUE !!!!
| PB | 0.23 | 1.8
| PP | 0.22 | 1.67
| PUR | 0.025 |  | PUR Foam 80/100
| PVC | 0.16 | 1.01
| PVDF | 0.12 | 1.38
| SOIL | 2.326
| STEEL | 67 | 0.45
| WATER | 0.582 | 4.2
| ICE |  | 336
RESULTS
TEMPERATURE DECREASE |  | K/m | -0.0062604 | DEGREE per METRE
TEMPERATURE DECREASE OVER WHOLE PIPE LENGTH |  | K | -3.1302 | DEGREES
SPECIFIC HEAT LOSS |  | W/m | -17.263 | WATT per METRE
TOTAL HEAT LOSS OVER WHOLE PIPE LENGTH |  | KW | -8.6315 | KILOWATT
HEAT TRANSMISSION NUMBER |  | W/m.K | 1.7263 | WATT per METRE per DEGREE
STAGNATING WATER
TIME TILL FREEZING STARTS |  | hrs
PERCENTAGE FROZEN WATER AFTER STAGNATION TIME |  | %
0.57927 | "= R1
0.0012521 | =B
#NUM! | =t(s)
43.1574 | =Q(v)
#NUM!